## Checklist
Item ID | Conditions | Description | Code | Note | Example | Link
A08 |  | Lifts are not exposed to weather | AS3000 | Lift opening to an outdoor area must protect electrical components from moisture ingress. | a08-weather-seal.png | https://example.com/examples/a08-weather-seal.png
A09 |  | Lifts do not open directly into a dwelling | SL |  | Provide a protected lobby between the lift and the dwelling entrance.
A10 | PitToEarth: FALSE | If pit is not to solid earth, need CWT safety device | EN81-20 | Counterweight safety gear required when pit is not founded on solid earth. | a10-cwt-safety.png | https://example.com/examples/a10-cwt-safety.png
A11 | MaxFFLInt: >11m | Must have lift-well emergency doors | EN81-20, RDM | Required where the travel between landings exceeds 11 m. | Add emergency doors at max 11 m spacing along the well.
A13 | BuildingClass: "Class 9b" OR MaxFFLInt: >=20 | Enhanced fire service controls | BCA | High-rise or assembly buildings need fire service lift controls. | Provide fire service control switch and compliant signage.
B01 |  | Pit structure designed for buffer impact loads | AS1170 |  | Confirm structural design accounts for buffer reaction forces.
B02 | FloorsServed: >=10 | Guide rail bracket spacing verified for travel | EN81-20 | Taller installations need verified bracket spacing. | Document guide-rail bracket spacing calculations.
C01 |  | Machine room power isolation provided | AS3000 |  | Install a lockable main switch for the lift supply.
C02 | PitToEarth: FALSE | Earthing of car and well per wiring rules | AS3000 | Earthing continuity required where pit is not to solid earth. | Measure and record earth continuity resistance.
F01 |  | DA Consent (NOD document) | SL
F02 |  | BCA Report | SL

## Inputs
Name | Type | Label | Unit | Choices | Default
PitToEarth | Boolean | Pit is founded on solid earth |  |  | TRUE
MaxFFLInt | Float | Max internal floor-to-floor travel | m |  | 0
FloorsServed | Integer | Number of floors served |  |  | 2
BuildingClass | Choice | Building classification |  | Class 2;Class 3;Class 9b | Class 2

## Sections
Prefix | Name | Scope
A | Architectural
B | Structural
C | Electrical
F | Reports | project

## Glossary
Term | Meaning
AS3000 | AS/NZS 3000 Wiring Rules — electrical installations standard. (sample text)
AS1170 | AS/NZS 1170 Structural design actions. (sample text)
EN81-20 | EN 81-20 — safety rules for the construction and installation of lifts. (sample text)
BCA | Building Code of Australia. (sample text)
DDA | Disability Discrimination Act — accessibility requirements. (sample text)
SL | State/local regulatory requirement. (sample text)
RDM | Reference Design Manual. (sample text)